安全知识---三氟化氮(NF3)安全操作实践

1. General概述

Nitrogen trifluoride (NF3) is a toxic, colorless, odorless, nonflammable, oxidizing compressed gas NF3offers the advantages of relative ease of use at ambient conditions and the ability to act as a fluorinating agent. Because of these factors, it has gained commercial acceptance in a number of applications. The electronics industry uses it in plasma and thermal cleaning applications for its advantages such as high etch rates, high selectivity, carbon-free etching, and minimal residual contamination. NF3 is also used as a fluorine source in high energy chemical lasers, owing to its ease of use relative to fluorine gas. NF3is also used as an intermediate in the production of specialized chemicals.

三氟化氮（NF3）是有毒、无色、无嗅、不可燃的氧化性压缩气体。NF3具有在室温条件下相对容易使用和可以用作氟化剂的优点。由于这些因素，它在许多应用中获得了广泛的认可。由于它的优点，如高蚀刻率、高选择性、无碳蚀刻和最小限度的残留污染，电子工业把它用在等离子和热清洁应用中。由于它相对于氟气更容易使用，NF3在高能化学激光器中用作氟源。在特殊化学品的生产中NF3还用作媒介。

NF3is available in a variety of grades and at purity levels in excess of 99.999 % due to advanced purification techniques developed by Air Products. Table 1 lists the physical and chemical properties of NF3.

NF3有多种等级，由于Air Products发展的先进的净化技术，还有纯度超过的99.999 %的NF3。表1列出了NF3的物理和化学性质。

2. Key Considerations关键的考虑

Health Effects对健康的影响

NF3 is not hazardous by skin contact and is a relatively minor irritant to the eyes and mucous membranes.

皮肤接触NF3是没有危险的。对于眼睛和黏膜，它是一个相对程度较轻的刺激物。

Over-exposure to NF3via inhalation induces the conversion of hemoglobin to methemoglobin. The formation of methemoglobin reduces the amount of oxygen available to body tissues. This can lead to chemical cyanosis, headache, dizziness, weakness, confusion, and other manifestations associated with a reduced oxygen supply. Hemolytic anemia, enlargement of the spleen, and pathologic changes in the liver, kidneys, and heart muscle may occur as secondary effects of methemoglobinemia, which is reversible. At the cessation of NF3exposure, methemoglobin reverts back to hemoglobin. While methemoglobinemia clears spontaneously over several hours, hemolytic anemia may take several weeks to resolve.

过量吸入NF3会导致血色素转化成高铁血红蛋白。高铁血红蛋白的形成减少了身体组织可以得到的氧的数量。这会导致化学黄萎病、头痛、眩晕、虚弱、昏聩和其它伴随着氧气供应减少的表现。作为高铁血红蛋白症的次要影响，会发生溶血性贫血、脾扩大和肝、肾、心肌的病变，这些影响是不可逆转的。在NF3暴露停止后，高铁血红蛋白转化回血红素。高铁血红蛋白症会在几个小时后自动消失，而溶血性贫血需要几个星期才能解除。

Toxicological Properties毒物学性质

Inhalation吸入 LC50 = 6,700 ppm (1 hour小时) rat鼠

For all species tested, the immediate effect of acute exposure to high concentrations of NF3 is extensive methemoglobin formation with subsequent hypoxia. This is often followed by hemolytic anemia that can cause liver, kidney, spleen, and sometimes heart effects. Vomiting has also been observed in dogs and monkeys that have inhaled NF3.

对于测试的所有物种，急性暴露于高浓度NF3的直接影响是大范围高铁血红蛋白形成和并发的组织缺氧。随后的通常是会导致肝、肾、脾和有时候的心脏病变的溶血性贫血。在已经吸入了NF3的狗和猴子身上还观察到了呕吐。

Exposure of rats to 100 ppm NF3 by inhalation for 7 hours per day, 5 days per week for 19 weeks resulted in mild to moderate pathological changes in the liver and kidneys. No other effects were noted. These chronic exposures failed to produce any measurable changes in the general appearance, appearance of teeth, activity, growth, mortality, blood, serum chemistry, or fluorine content of the teeth and bones of the rats tested.

老鼠通过吸入暴露在100 ppm NF3 中连续19周，每周5天，每天7小时，导致了肝和肾的轻微到中度的病变。没有注意到其它影响。这些长时间的暴露没有在被测试老鼠的总体外观、牙齿外观、活动性、生长、死亡率、血液、血清化学性质或牙齿和骨骼的氟含量方面产生任何可测量的变化。

NF3 has been found to be weakly mutagenic in bacterial cells and non-mutagenic in animal cells and whole animal test systems.

已经发现，在细菌细胞内NF3是轻微的诱导有机质突变的物质，而在动物细胞和整个动物测试系统内NF3不会诱导有机质突变。

Exposure Levels暴露水平

The National Academy of Sciences—National Research Council, Committee of Toxicology, has recommended an Emergency Exposure Limit (EEL) for NF3 of 22,500 ppm. This is based upon actual measurements which indicate that exposure of up to 30,000 ppm x min did not cause any negative health effects in laboratory animals, while anemia did occur at exposures of 120,000 ppm x min.

国家科学院—国家研究理事会毒物学委员会已经推荐的NF3紧急暴露极限(EEL)为22,500 ppm。这是基于实际测量的。该测量显示，大到30,000 ppm x min的暴露不会在实验室动物身上导致对健康的负面影响，而当暴露达到120,000 ppm x min时确实发生了贫血。

The EEL is a concentration that is believed not to result in a period of disability or interfere with the performance of tasks. While exposure at these levels may produce injury, the injury would be reversible. The EEL represents a cumulative exposure limit taking into account both the time of exposure and the concentration at which the exposure occurs. Any combination of time of exposure and concentration that is less than the recommended level of 22,500 ppm x min is acceptable. Table 2 illustrates acceptable exposure times for varying concentrations of NF3 in air at the EEL of 22,500 ppm x min.

EEL是这样一个浓度，在此浓度下不会导致一段时间的无力或妨碍完成任务。虽然在这种水平的暴露可能导致伤害，但伤害是可逆的。EEL代表了一个既考虑了暴露时间又考虑了暴露发生时的浓度的累积的暴露极限。任何小于22,500 ppm x min的推荐水平的暴露时间和浓度的组合都是可以接受的。表2说明了在22,500 ppm x min的EEL下，对于空气中不同的NF3浓度可以接受的暴露时间。

The TLV-TWA (10 ppm or 29 mg/m3[ACGIH,1997]) for NF3 was set by the American Conference of Governmental Industrial Hygienists at one-tenth the test level of the previously cited 19-week study under Toxicological Properties.

美国政府工业卫生学者会议把NF3的TLV-TWA (10 ppm或29 mg/m3[ACGIH,1997])设定为前面在“毒物学性质”下引用的19周研究的测试水平的十分之一。

Tables 3, 4 and 5 provide detailed information on the TLV-TWA, Immediately Dangerous to Life and Health (IDLH) concentrations, and Acute Toxicity, LC50 levels for common gases used in wafer fabrication.

表3、4和5提供了用于晶片制造的常用气体的关于TLV-TWA水平、立即危及生命和健康的浓度水平、剧毒LC50水平的详细资料。

Table 1 Physical and Chemical Properties表1 物理和化学性质

(NF3 is a colorless gas. Trace quantities of impurities can impart a musty or pungent odor to the gas.)

NF3是无色气体。痕量的杂质会使气体带有一种霉味或刺激性气味。

Melting Point熔点 –340.2°F (–206.8°C)

Boiling Point沸点 –200.2°F (–129°C)

Critical Temperature临界温度 –38.5°F (–39.3°C)

Critical Pressure临界压力 44.02 atm (4.46 MPa)

Liquid Density液体密度 (atm at Boiling Point在沸点)  97.13 lb/ft3(1554 kg/m3)

Gas Density气体密度 (atm, 70°F)  0.184 lb/ft3(2.95 kg/m3)

Heat of Vaporization at Normal Boiling Point正常沸点时的蒸发热 2.77 kcal/mol (11.60 kj/mol)

Heat of Fusion熔解热  0.095 kcal/mol (0.40 kj/mol)

Specific Gravity比重 (70°F, air空气=1) 2.503

Specific Volume比容 (70°F, atm) 5.43 ft3/lb (0.339 m3/kg)

Standard Enthalpy of Formation at 0 K  0 K时的生成标准焓 –28.43 kcal/mol (–119.03 kj/mol)

Standard Enthalpy of Formation at 298 K  298K时的生成标准焓 –29.80 kcal/mol (–124.77 kj/mol)

Standard Entropy at 298 K  298 K时的标准熵 62.2 cal/mol-K (260.5 j/mol-K)

Gibbs Free Energy of Formation at 298 K  298 K时的吉布斯生成自由能 –21.4 kcal/mol (–89.6 kj/mol)

Heat Capacity at 298 K at Constant Pressure 298 K时的恒压热容 12.79 cal/mol-K (53.54 j/mol-K)

Molecular Weight分子量 71.002

Geometry几何形状  Pyramidal金字塔形

N-F Bond Length N-F键长 1.37 Angstroms

N-F Bond Angle  N-F键角  103 Degrees

Mean Bond Energy 平均键能 66.4 kcal/mol (278.0 kj/mol)

Dipole Moment 偶极矩 .234 D

Solubility (slightly soluble in water)溶解性（微溶于水） 1.43 x 10-5mole fraction at 1 atm/22°C

Table 2. Acceptable Exposure Times for Varying Concentrations of NF3in Air (EEL=22,500 ppm x min)

表2 对于空气中不同的NF3浓度，可以接受的暴露时间(EEL=22,500 ppm x min)

Time of Exposure (min) 暴露时间（分钟）

Concentration (ppm)浓度

1 22,500

10 2,250

30 750

60 375

Source: “Recommendation for Revised Emergency Exposure Limits for Spills of NF3,” NAS/NRC Committee

on Toxicology, 1974.

来源：“关于修改的NF3逸出紧急暴露极限的建议”，NAS/NRC毒物学委员会，1974年。

Reactivity反应活性

Reactivity is similar to that of oxygen at room temperature. NF3 is relatively inert at ambient temperature and pressure conditions and exhibits little, if any, reactivity. However, at higher temperatures (>300°C), NF3 will dissociate into reactive fluorine species that react with most materials. These reactive species can lead to uncontrolled reactions with polymers and certain metals, liberating heat and causing further dissociation of NF3. As temperatures increase above 400°C, the reactivity of NF3 becomes more like that of fluorine. Therefore, avoid conditions and/or mechanisms that could lead to the inadvertent heating of NF3.

反应活性与室温下的氧相似。在常温常压下NF3是相对不活泼的，显示出很低，如果说有的话，的反应活性。但是，在更高的温度(>300°C)时，NF3将分解成活泼的能同大多数物质反应的氟。这些活泼的氟会导致无法的控制的同聚合体和特定金属的反应，释放出热量，导致NF3的进一步分解。当温度上升到400°C以上时，NF3的反应活性变得更象氟。因此，要避免可能导致无意中对NF3加热的条件和/或机制。

For example, one such mechanism—adiabatic compression—occurs when high-pressureNF3 is introduced rapidly into a low-pressure dead-end space. The resulting rise in gas temperature may be sufficient to cause the dissociation of NF3.

例如，当把高压引入一个低压的密闭空间时，一种这样的机制—绝热压缩就会发生。所导致的气体温度的上升可能足以导致NF3的分解。

NF3 is often used in concert with other gases such as silane in the processing of semiconductors. Related information regarding reactivity involves Air Products’ flammability testing of NF3/Silane (SiH4) mixtures, which yielded consistent results with those reported at the Chemical Technology Research Lab in Tokyo, Japan in 1990. The lower and upper flammability limits (LFL and UFL) for SiH4 in NF3 are 0.66% and 95.3%, respectively. In other words, in a binary blend of SiH4 and NF3, concentrations of silane greater than or equal to 0.66% and less than or equal to 95.3%, form an explosive mixture. Dilution with nitrogen (N2) provides a three-component flammability limit of 2.0% SiH4/2.5% NF3/95.5% N2. Although the LFL for SiH4 increases to 2.0% with the addition of N2, the large range of flammability still exists. To achieve safe operating conditions in a system using SiH4 and NF3, dilution with N2 is required to remain outside the flammability limits. Table 6 indicates the magnitude of the flammability range of SiH4 and H2 blends of NF3, O2 and air, respectively.

NF3经常同其它气体，如硅烷一起用于半导体的处理。关于反应活性的相关资料包括Air Products的NF3/硅烷(SiH4)混合物的可燃性测试。该测试得到的结果同1990年日本东京的化学技术研究实验室报道的结果相一致。在NF3中的硅烷的可燃下限和上限分别是0.66%和95.3%。换句话说，在硅烷和NF3的二元混合物中，硅烷的浓度大于或等于0.66%和小于或等于95.3%，都会形成爆炸性混合物。用氮(N2) 稀释后的三组分的可燃极限为2.0% SiH4/2.5% NF3/95.5% N2。尽管随着氮的加入，硅烷的LFL增加到2.0% ，可燃范围仍然很大。为了在使用SiH4和NF3的系统里得到安全的操作条件，要求用氮稀释，使之保持在可燃极限以外。表6说明了SiH4和H2分别在NF3、O2和空气中的混合物的可燃范围的大小。

Environmental Impact对环境的影响

NF3 can be manufactured, used, and disposed of in a safe and environmentally responsible manner. NF3 poses a minimal environmental hazard due to its non-reactivity and insolubility in water under normal conditions

可以通过一种安全的对环境负责的方式来制造、使用和处理NF3。由于它的不活泼性和正常状态下在水中的不溶解性，NF3几乎不会造成环境危害。

Air Products has sponsored research at the Massachusetts Institute of Technology to study the reactivity of NF3 in the atmosphere. Also, Air Products continues to conduct and/or support the analysis of emissions from semi-conductor manufacturing production tools.

Air Products已经在麻省理工学院赞助了在空气中NF3的的反应活性的研究。Air Products还一直进行和/或支持来自半导体工业生产工具的辐射的分析。

NF3 has negligible impact on ozone depletion. The photolysis of NF3 in the stratosphere yields a fluorine radical that reacts fairly rapidly to form hydrogen fluoride (HF). The stability of HF results in an ozone-depleting potential of the fluorine radical that is approximately three orders of magnitude less than that of the chlorine radical. NF3 has a relatively short atmospheric lifetime (740 years) and dissociates more readily than C2F6 and CF4.HF ultimately diffuses down to the troposphere where it is removed by wet deposition.

NF3对于臭氧损耗几乎没有影响。在同温层里NF3的光解作用氟原子团，氟原子团相当迅速地发生反应，生成氟化氢(HF)。HF的稳定性导致了氟原子团的臭氧损耗的可能。氟原子团大约比氯原子团小三个数量级。NF3具有相对短的大气寿命（740年），比C2F6和CF4.更容易分解。HF最终扩散到大气中，在大气中它通过湿沉积被除去。

Due to the low solubility of NF3 in water (1.43x 10-5 mole fraction at 1 atm partial pressure of NF3 and 22°C) and its non-reactivity with water under normal conditions, the environmental hazards of an NF3 leak at sea, or in coastal waters during shipment, are minimal. Any large release of NF3 would dissipate before significant concentrations of gas could build up in water.

由于NF3在水中的低溶解性（在22°C和NF3的分压为1 atm时为1.43x 10-5）和通常条件下它同水不反应，在运输过程中，在海洋或海岸的NF3泄露的环境危害是最小的。在有意义的气体浓度在水中能够积累起来之前，任何大量释放的NF3都已经弥散了。

Abatement消除

Air Products will assist customers in determining and implementing appropriate methods to control and monitor NF3 emissions. The method and degree of control, and regulatory compliance, is the ultimate responsibility of the end user. If your facility implements an abatement policy, please contact your Air Products representative for specific recommendations.

在决定和实施合适的方法来控制和监测NF3的扩散方面，Air Products会帮助用户。控制的方法与程度和与法规的一致性是终端用户的根本责任。如果你的设备要实施一项消除策略，请同Air Products的代表联系，寻求具体的建议。

3. Maintaining User Safety维护用户的安全

Material Release 材料释放

If a leak develops in a customer system, close the cylinder valve and vent residual product, and purge the lines with inert gas before attempting repairs. Use appropriate protective equipment (SCBA).

如果在用户的系统里发生了泄露，关闭阀门并排出残余产品。在试图修理之前，用惰性气体净化管道。使用合适的防护装备（SCBA）。

Leaks occurring at the cylinder valve’s pressure relief device, diaphragms, or valve to the cylinder connection cannot be repaired.

发生在钢瓶阀门的减压装置、横膈膜或阀门到钢瓶的接头处的泄露不能维修。

Attempts to repair these leaks may result in catastrophic failure of the package.

试图修理这些泄露会导致包装的灾难性故障。

If such a leak develops, or the cylinder valve cannot be closed, immediately contact the Air Products’ Emergency Response System at these numbers:

如果发生了这样的泄露，或者钢瓶阀门无法关闭，立刻同Air Products的紧急反应系统联系：

•Continental U.S., Canada & Puerto Rico美国大陆、加拿大和波多黎各:(800) 523-9374

•Other Locations其它地方: (610) 481-7711

Fire Control起火控制

NF3 cylinder valves are equipped with pressure relief devices consisting of a frangible rupture disc backed by a fusible alloy. This allows the cylinder contents to be released, preventing cylinder failure under fire conditions. The disc is designed to burst at 3400psig and the alloy will melt at 74°C. Both conditions must be met before the pressure release device will vent. Although NF3 is non-flammable, it will vigorously support combustion. Do not use HALON 1301, dry ammonium phosphate, or bicarbonate on NF3 fires because they produce toxic by-products.

NF3钢瓶配备有由易碎破裂盘及其后的易熔合金组成的减压装置。在起火的情况下，它允许钢瓶内容物被释放出来，防止钢瓶发生故障。破裂盘设计得在3400psig的压力下破裂，合金在74°C时熔化。在减压装置排气之前，两个条件都要被满足。尽管NF3是不可燃的，它会有力地支持燃烧。不要在同NF3有关的火焰上使用HALON 1301、干磷酸铵或重碳酸盐，因为它们产生有毒副产品。

Use carbon dioxide (CO2) extinguishers to extinguish small fires. Use large amounts of water to extinguish fires covering a large area. Although NF3 is not water soluble, many of the toxic by-products such as HF are water soluble. The best extinguishing method requires large amounts of liquid nitrogen (LIN) to provide a non-reactive environment and act as a heat sink.

使用二氧化碳(CO2)灭火器来熄灭小火。使用大量的水来熄灭覆盖面积很大的火焰。尽管NF3不溶于水，许多的有毒副产品，如HF是可溶于水的。最好的灭火方法是用大量的液氮(LIN)来提供一个不反应的环境，同时作为热接收器。

First Aid Treatment急救处理

An individual exhibiting symptoms of acute NF3 poisoning from concentrations in excess of 6,000 ppm should be removed from the contaminated area as quickly as possible. Then oxygen therapy should be started at once by trained personnel, and a physician should be notified immediately.

应该把表现出超过6,000 ppm浓度的剧烈的NF3中毒症状的人员尽快从污染区域转移走。接着由经过训练的人员立刻开始进行氧气治疗，并且应该立刻通知医生。

Observe these follow-up first-aid measures:

遵守下列急救措施：

•Continue therapy for up to six hours.继续治疗6个小时以上。

•Individual should rest under close supervision until all possibility of secondary complications can be discounted.患者应在密切监视下休息，直到所有二次并发症的可能性减小为止。

•Be aware of possible anemia and impaired kidney functions.知道可能发生贫血和肾功能减弱。

•Individual should receive follow-up examinations by a physician.患者应该接收随后的医生检查。

Table 4. IDLH: Immediately Dangerous to Life and Health

表4 IDLH：立即危及生命和健康

AsH3  3

Cl2  10

HF  30

HCl  50

H2S 100

NO  100

NH3 300

NF3  1000

CO  1200

Source来源: NIOSH

Table 3. TLV-TWA of Common Gases in Wafer Fabrication

表3 晶片制造中常用气体的TLV-TWA

AsH3 0.05

PH3 0.3

Cl2 0.5

HF  3 STEL Ceiling上限

HCl  5 STEL Ceiling上限

H2S 10

NF3 10

CO  25

NH3 25

NO 25

N2O 50

Source来源: 1997 TLVs® and BEIs®, ACGI®

Table 5. Acute Toxicity LC50

表5 剧毒性LC50

AsH3 20 ppm

NO  115 ppm

Cl2 293 ppm

H2S 712 ppm

HF  1300 ppm

HCl  3120 ppm

CO  3760 ppm

NF3  6700 ppm

NH3 7338 ppm

Source来源: CGA

4. Materials Compatibility材料相容性

Metals金属

Clean and degrease all metals coming into contact with NF3 using detergent or suitable cleaning agents that are free of finely divided metal chips and particles. Passivation of the system using concentrations of 5-10% fluorine in an inert gas is recommended to prepare the system. Thoroughly clean and dry the system prior to passivation procedures.

使用洗衣粉或没有金属粉末和颗粒的合适的清洗剂来为接触NF3的所有金属去污和去油。推荐使用氟浓度为5%到10%的惰性气体里钝化系统，为系统使用做好准备。在钝化程序之前，彻底地清洁和干燥系统。

Gaseous NF3 containing 0.1% or less active fluorides (calculated as HF) was found to be noncorrosive toward several different parent and welded metal specimens. During static exposure of aluminum, stainless steel, Inconel®, Monel®, nickel, titanium, steel, copper, beryllium copper, aluminum bronze, maraging steel, and tungsten, no metal exhibited corrosion penetration rates greater than 0.43 mils per year (mpy). Generally, a corrosion penetration rate of 1 mpy or less is considered acceptable for long-term compatibility. The tests were conducted for 270days at temperatures ranging from –78°C to71°C and pressures ranging from 2 x 10-7 to 2.5 x 10-6 psi.

含有0.1%或更少的活泼氟化物（认为是HF）的气态NF3被发现对于几种不同的母材和焊接金属试验品是没有腐蚀性的。在铝、不锈钢、因康镍合金、蒙乃尔铜镍合金、镍、钛、钢、铜、铍铜、铝铜、马氏体钢和钨的静态暴露过程中，没有金属显示出大于0.43密耳每年（mpy）的腐蚀穿透率。一般来说，认为1 mpy或更小的腐蚀穿透率对于长期的相容性来说是可以接受的。测试进行270天，温度范围从–78°C到71°C，压力范围从2 x 10-7 到2.5 x 10-6 psi。

Carbon steel, stainless steel, nickel and its alloys, and copper are suitable materials of construction for low-pressure service (<70 psig) and temperatures up to 150°C. For pressures up to 1450 psig at ambient temperatures, carbon steel and stainless steel are suitable materials. For high-pressure and higher temperature service, nickel and certain alloys of nickel and copper are preferred. Most metals will react with NF3 at temperatures in excess of 300°C.

碳素钢、不锈钢、镍及其合金和铜是低压(<70 psig)设施和大到150°C的温度的合适的建材。对于室温下大到1450 psig的压力，碳素钢和不锈钢是合适的材料。对于高压和高温设施，镍同镍和铜的特定合金是首选。在温度超过300°C时，大多数金属都会和NF3发生反应。

The presence of contaminants in the system can significantly affect the corrosion resistance and compatibility of many metals. For example, both HF and water decrease the corrosion resistance and compatibility of metals exposed to NF3, and both impurities should be minimized. The presence of fingerprints, halocarbon oils, and machine oils have been shown to significantly reduce the temperature resistance of metals, including stainless steel and nickel.

在系统内存在污染物会大大地影响许多材料的抗腐蚀性和相容性。例如，HF和水都会降低暴露于NF3的金属的抗腐蚀性和相容性，要最大程度地减少这两种杂质。已经证明，手印、卤烃油和机油的存在会大大降低包括不锈钢和镍在内的金属的抗温度能力。，

Non-metals非金属

All non-metal components should be thoroughly cleaned and free of oils, grease, and dirt using either detergent or a suitable cleaning agent. Thoroughly clean and dry the components prior to use. Highly fluorinated polymers such as Teflon®, Viton®, Kel-F®, or Neoflon® are materials of choice. Studies have shown that PTFE(Teflon) is the most compatible at temperatures up to 150°C.

应该使用洗衣粉或合适的清洁剂来对所有的非金属组件彻底清洗和去除油、润滑脂和污垢。在使用之前，彻底地清洗和干燥组件。高氟化聚合体，如特氟纶、氟化橡胶、Kel-F或氟塑料46是可以选择的材料。研究已经显示，在温度高到150°C时PTFE（特氟纶）是最相容的。

Lubricants润滑剂

Use of per fluorinated lubricants (Krytox® or Fomblin®) for vacuum pumps in NF3 service is recommended. Hydrocarbon lubricants can react violently with NF3 and should not be used. NF3 dissolves some halocarbon greases.

推荐在NF3设施中的真空泵上使用氟化润滑剂（Krytox® 或Fomblin®）。碳氢润滑剂能够同NF3剧烈反应，不能使用。

5. Supply Systems供给系统

NF3 is available in seven types of high-pressure containers including cylinders, Y cylinders, and tube trailers.

可以在七种类型高压容器，包括钢瓶、Y钢瓶和管道拖车中得到NF3。

Leak-checking NF3 cylinders prior to service is recommended. After placement in a gas cabinet, the cylinder valve should be checked for trace leaks at the valve connection, valve stem, pressure relief device, and cylinder/valve connection. Similar steps should be taken for Y cylinders and tube trailers. Either of the following techniques should be used:

推荐在工作之前对NF3钢瓶检漏。在放入气体室后，应该检查钢瓶阀门在阀门接头、阀杆、减压装置和钢瓶阀门接头处是否有微量泄露。对于Y钢瓶和管道拖车应该采取相似的步骤。应该使用下列技术中的一个：

•An electron-capture type halogen leak detector or an NF3 point detector can be used. Refer to the list of monitor suppliers at the end of this section.可以使用电子俘获型检漏仪或NF3点检漏仪。请参考本文结尾处的监控器供应商列表。

•GASGUARD® systems will perform pressure and vacuum decay testing of the cylinder connection to the gas system as part of the standard control software configuration. 作为标准控制软件配置的一部分，GASGUARD®系统将进行钢瓶到气体系统的接头的压力和真空衰减测试。

GASGUARD® Gas Cabinets  GASGUARD®气体室

NF3 should be delivered from a system within an exhausted enclosure with proper and continuous ventilation. When using bulk supply of NF3, such as a Y cylinder or a tube trailer, the pigtail-to-valve connection should also be ventilated.

应该从带有适当和连续的通风的耗尽室内的系统传输NF3。当需要大量供应NF3时，如Y钢瓶或管道拖车，还应该对猪尾管到阀门接头通风。

Purging of the gas systems with a dry, inert gas such as nitrogen or argon, is recommended prior to breaking any connection of the gas system. Automation provided by GASGUARD systems ensures thorough and complete purging of the gas delivery system.

在断开系统的任何连接之前，推荐用干燥惰性气体，如氮或氩来净化气体系统。GASGUARD系统提供的自动操作确保了气体传输系统的彻底和完全的净化。

Process Lines过程管道

Gas distribution lines for NF3 service should be fabricated from compatible materials and thoroughly cleaned to remove any oxidizable material. The following steps are crucial for adequate line preparation:

用于NF3设施的气体分配管道应该采用相容的材料制造，并彻底清洁以去除任何可氧化材料。下列步骤对于适当的管道准备是至关重要的：

•Clean the line thoroughly with an appropriate cleaning agent and dry with oil-free nitrogen or helium. Shop compressor air should not be used because oil mist will recontaminate the line. Be alert for any dead space where degreasing agents can be trapped.使用合适的清洗剂彻底清洗管道，并用无油氮气或氦气吹干。

•Inspect the system for any indications of reaction, leaks, changes in mass flow, or changes in delivery pressure across line filters.检查系统是否有任何反应、泄露、大量流动的变化或通过管道过滤器的传输压力的变化的迹象。

• NF3 leaks in a process line or equipment may be detected by the two techniques mentioned previously.可以通过前面提到的两种技术来检测在过程管道或设备里的NF3泄露

Ventilation通风

NF3 has no detectable odor, so forced air/exhaust ventilation and ambient air monitoring are recommended where NF3 is stored or used. Ventilation ducts should be designed for high-flow interference. Standard flow ventilation requirements for gas cabinets adequate for NF3 include average face velocity of 200 fpm at access ports with 150 fpm as the minimum velocity at any point. Laminar flow is strongly recommended for non-load lock systems.

NF3没有可以探测到的气味，所以推荐在储存和或使用NF3的地方采用强迫通风/排气通风。NF3气体室的标准流量通风的要求包括在入口处的平均面速度为200 fpm和在任一点的最小速度为150 fpm。

Monitors监测器

NF3-specific detectors are highly recommended since NF3 has no detectable odor. Prolonged breathing of high concentrations of NF3 should be avoided. The most accurate technique for NF3 detection is infrared spectral absorption in the 11 micron (900 cm-1) region.

由于NF3没有可探测到的气味，强烈推荐使用NF3专用探测器。应该避免长时间呼吸高浓度NF3。用于NF3探测的最精确的技术是在11微米波段的红外吸收光谱。

Suppliers of monitors include监测器供应商包括:

•CEA Instruments, Inc.16 Chestnut Street Emerson, NJ 07630

Tel电话: (201) 967-5660

•EIT251 Welsh Pool Road Exton, PA 19341

Tel: (800) 872-8008

•Enmet Analytic680 Fairfield Court Ann Arbor, Ml 48106

Tel: (313) 761-1270

•Foxboro Company600 North Bedford Street East Bridgewater, MA 02333

Tel: (508) 378-5400 or(888) 369-2676, Ext. 5556

•Gas Tech Inc.

8407 Central Avenue Newark, CA 94560

Tel: (510) 745-8700

•Telosense Corporation5369 Randall Place Fremont, CA 94538

Tel: (510) 490-2087

•Zellweger Analytics, Inc.

405 Barclay Boulevard Lincolnshire, IL 60069

Tel: (800) 323-2000

6. Safety Issues安全问题

The following general safeguards are important in handling NF3.

在操作NF3中，下列的通用安全措施是很重要的：

•Avoid conditions that can result in high temperatures, such as adiabatic compression, from the rapid pressurization of a system.避免可能导致来自系统迅速加压的高温的条件，如绝热压缩。

•Do not attempt purification of NF3 via adsorption.禁止试图通过吸附来净化NF3。

•Stainless steel and copper are suitable materials of construction for low-pressure service.对于低压设施，不锈钢和铜是合适的建材。

•If elastomers must be used, Teflon and materials are acceptable for NF3 service.如果必需使用人造橡胶，对于NF3，特氟纶和Kel-F是可以接受的材料。

•Ball valves are not recommended for general use in NF3 service due to the potential for adiabatic compression in closed downstream systems occurring as the result of the rapid opening of this type of valve. Use of ball valves should be restricted to isolation functions only. Any valve that is used in NF3 service should be opened slowly to prevent adiabatic compression.迅速地开启这种类型的阀门，会导致在密闭回流系统内发生绝热压缩的可能性，因此在NF3设施中一般不推荐使用球阀。

•All components should be free of grease, oil, and other contaminants. It is recommended that procedures for cleaning systems for oxygen service as described in CGA Pamphlet G-4.1 be used.所有组件必须没有润滑脂、油和其它污染物。推荐使用用于氧设施的清洁系统程序，CGA 手册G-4.1描述了这种程序。

•The operation of high-pressure systems should be done remotely and by personnel wearing appropriate personal protective equipment. Air Products’ GASGUARD line of gas delivery systems provides an excellent means to minimize direct operator contact by providing an external control interface.应该由穿戴着适当的个人防护装备的人员遥控操作高压系统。通过提供外部控制界面，Air Products的GASGUARD气体传输系统提供了一种最大限度的减少操作员直接接触的极好的方式。

•Observe the same measures and precautions necessary for the safe handling of any compressed gas.遵守对于任何压缩气体的安全操作都是必要的同样的措施和防范。

• NF3 cylinders must be securely supported while in use to prevent movement and straining of connections. Always protect NF3 cylinders from mechanical shock or abuse. Never heat NF3 cylinders with a torch, heat lamp, or water bath.

在使用时，必须固定支撑NF3钢瓶，以防止移动和接头的变形。总是要保护NF3钢瓶，防止机械冲击或损伤。禁止用火炬、热灯或水浴来加热NF3钢瓶。

In some delivery systems, NF3 may be subjected to adiabatic compression. This can occur when a valve between a high-pressure gas source and a low-pressure flow circuit is opened quickly. As gas enters such spaces and rapidly comes to a higher pressure, shock waves may be dissipated on material surfaces in a very short time. When high gas temperatures are expected, systems designed for such service should avoid the use of plastics or polymers in contact with gas-wetted surfaces. In addition, rapid-opening valves, such as ball valves, should be restricted to use only as isolation valves in NF3 service.

在一些传输系统里，NF3可能受到绝热压缩。当迅速开启在高压气源和低压气流回路之间的阀门时，会发生绝热压缩。当气体进入这样的空间并迅速地接触到更高的压力时，冲击波会在非常短的时间内消耗在材料表面。当预计气体温度比较高时，设计用于这种设备的系统要避免在接触气体的表面使用塑料或聚合体。另外，在NF3设施中，应该把迅速开启的阀门，如球阀限制得只能用作隔热阀。

Purification processes using dry media, such as activated charcoal (carbon) or molecular sieve, may be subject to rapid exotherms from sudden exposure of the media to large quantities of NF3.

由于介质突然暴露在大量的NF3中，使用干燥介质，如活性炭或分子筛的净化过程可能造成温度迅速上升。

Air Products does not recommend purification adsorption of NF3.

Air Products不推荐NF3的吸附净化。

7. For More Information为了更多的资料

Obtain additional NF3 product safety information by contacting the Air Products Technical Information Center at (800) 752-1597. Or contact our MSDS Fax-On-Demand Safety Information number—(800) 245-2746, which is available24 hours a day. Request MSDS ID# 1076.Or visit the Air Products’ Web site at www.51qiti.com .

要得到另外的NF3产品安全资料，可以同Air Products的技术资料中心联系，电话是(800) 752-1597；或者同我们的根据要求传真MSDS安全资料的号码(800) 245-2746联系，索要MSDS ID# 1076。该号码是全天24小时开通的。或者访问Air Products的万维网网址：www.51qiti.com 。

Trademarks and Registered Trademarks商标和注册商标:

• Fomblin® is a registered trademark of Foro Buonaparte 31. Fomblin®是Foro Buonaparte 31的一个注册商标

• Inconel® is a registered trademark of Inco Alloys International, Inc.

• Kel-F® is a registered trademark of Daikin.

• Krytox® is a registered trademark of DuPont Company.

• Monel®is a registered trademark of Inco AlloysInternational, Inc.

• Neoflon®is a registered trademark of Daikin.

• Teflon®is a registered trademark of DuPont Company.

• Viton® is a registered trademark of DuPont Company.

Rescue in Oxygen-deficient Atmospheres缺氧空气里的救援

Fiction: I can hold my breath long enough to rescue a downed co-worker.

虚构：我能够屏住呼吸足够长的时间来营救倒下的工友。

Fact: Over 50% of the workers who die in confined spaces are attempting to rescue other workers.

事实：超过50%的死在狭窄空间的工人正在试图营救其他工人。

Never enter an oxygen-deficient atmosphere (<19.5% O2) without self-contained breathing apparatus.

禁止未戴自给式呼吸器进入缺氧空气（氧含量小于19.5%）。

Emergency Response System紧急反应系统

• Call呼叫: +1 (800) 523-9374 (Continental U.S. and Puerto Rico美国大陆和波多黎各)

• Call呼叫: +1 (610) 481-7711 (Other locations其它地方)

• 24 hours a day, 7 days a week一天24小时，一周七天

• For assistance involving Air Products and Chemicals, Inc. gases and equipment.

Technical Information Center技术资料中心

• Call呼叫: +1 (800) 752-1597 (U.S美国.)

• Call呼叫: +1 (610) 481-8565 (Other locations其它地方)

• Fax传真: +1 (610) 481-8690

• E-mail电子邮件: gasinfo@apci.com

• Monday星期一–Friday星期五, 8:00 a.m.–5:00 p.m. EST

Product Safety Information产品安全资料

• For MSDS and Safety grams需要材料安全数据表和安全程序:

www.51qiti.com  stewardship

• Fax-on-Demand应要求发传真:

Call呼叫: +1 (800) 245-2746

• Enter MSDS Index No. 1000 for a complete list of available safety literature.

进入材料安全数据表第1000号可以获得现有的安全文献的全部目录

• 24 hours a day, 7 days a week一天24小时，一周七天